INFORMATION RELATIVE TO

THE DRAFT TITLE V OPERATING PERMIT

January 21, 2015

FOR:

Mississippi Power Company

Chevron Cogeneration Plant

200 Industrial Road, Gate 4

Pascagoula, Mississippi (Jackson Co.)

Permit No. 1280-00048

FACILITY DESCRIPTION

Mississippi Power Company, Chevron Cogenerating Plant is an existing steam electric power plant (SIC 4911) located in Pascagoula, Mississippi (Jackson County).  The plant generates electric energy for sale.  The facility combusts natural gas and refinery gas to produce steam, which is used to drive turbines that turn an electric generator.  The exhaust gases from the turbine are sent to a heat recovery steam generator (HRSG) that utilizes the waste heat to produce additional steam that is used to produce additional electricity.  The facility is applying for reissuance of their Title V Operating Permit and is not requesting any significant modifications to their existing operations.  The facility consists of the following emissions points:

| Emission Point | Description |
| --- | --- |
| AA-001 | 305.9 MMBtu/hr natural gas/refinery fuel gas fired GE Model L combustion turbine with heat recovery steam generator (HRSG). |
| AA-002 | 305.9 MMBtu/hr natural gas/refinery fuel gas fired GE Model L combustion turbine with heat recovery steam generator (HRSG). |
| AA-003 | 455.9 MMBtu/hr natural gas/refinery fuel gas fired GE Model M combustion turbine with supplemental-fired heat recovery steam generator (HRSG). |
| AA-004 | 455.9 MMBtu/hr natural gas/refinery fuel gas fired GE Model M combustion turbine with supplemental-fired heat recovery steam generator (HRSG). |
| AA-005 | 1084.6 MMBtu/hr natural gas fired ABB Model Number GT11N combustion turbine equipped with ABB dry low-NOX combustor system and heat recovery steam generator (HRSG). |
| AA-006 | 221.3 MMBtu/hr natural gas fired Wabash skid-mounted boiler. |
| AA-007 thru AA-011 | Storage Tanks (Insignificant Activities) |
| AA-012 and AA-013 | 2 – 300 horsepower (0.7623 MMBTU/hr) Cummings diesel fired black start-up engines. |
| AA-014 | 20 horsepower Briggs and Stratton propane fired UPS backup generator engine. |

This permit is not believed to trigger or require a Prevention of Significant Deterioration (PSD) review as a result of this renewal; however, the facility is a fossil fuel-fired steam electric plant totaling more than 250 million BTU/hr heat input with emissions that exceed 100 (and 250) tons per year for a criteria pollutant.  Since emissions do exceed the PSD thresholds, the facility is classified as a major PSD source; however, the facility is proposing no modifications at this time.

REVISIONS TO DRAFT PERMIT SINCE PREVIOUS PUBLIC NOTICE

The previous draft permit contained language requiring compliance with the Clean Air Interstate Rule (CAIR) since that rule was in effect at that time. CAIR is no longer in effect. For Emission Points AA-001 through AA-005, the permittee will be required to comply with the provisions of the Cross State Air Pollution Rule (CSAPR) as set forth 40 CFR 97 Subpart BBBBB - TR NOx Ozone Season Trading Program.

In response to comments received from EPA Region IV on December 1, 2014, the MDEQ has revised Section 1 of the draft permit to include a permit condition specifying the conditions under which a permit will be reopened, according to the provisions at 11 Miss. Admin. Code Pt. 2, R.6.4.G.  Condition 1.4 in Section 1 was added to the draft permit. This comment is applicable to all Mississippi Title V permits; therefore, all Mississippi Title V air permit will include this reopener language.

TITLE V PROGRAM APPLICABILITY BASIS

The facility’s potential to emit exceeds the Title V threshold limits of 100 tons per year (TPY) for Particulate Matter (PM), Sulfur Dioxide (SO2), Nitrogen Oxides (NOX), and Carbon Monoxide (CO).

LEGAL AND FACTUAL BASIS FOR DRAFT PERMIT CONDITIONS

The State and Federally-enforceable conditions of Title V Operating Permits are based upon the requirements of the State of Mississippi Air Emissions Operating Permit Regulations for the Purposes of Title V of the Federal Clean Air Act (11 Miss. Admin. Code Pt. 2, Ch. 6.), and applicable requirements effective upon the date of permit issuance.  Applicable requirement means all of the following as they apply to emissions units in a Title V source:

1.	any standard or other requirement set forth in the State Implementation Plan (SIP) approved or promulgated by EPA through rulemaking under Title I of the Federal Clean Air Act (Federal Act) including the following:

a.	most of the State of Mississippi Air Emission Regulations for the Prevention, Abatement, and Control of Air Contaminants (11 Miss. Admin. Code Pt. 2, Ch. 1.)

b.	the State of Mississippi Regulations for the Prevention of Air Pollution Emergency Episodes (11 Miss. Admin. Code Pt. 2, Ch. 3.),

c.	the State of Mississippi Regulations for the Prevention of Significant Deterioration of Air Quality (11 Miss. Admin. Code Pt. 2, Ch. 5.), and 40 CFR Part 52.21 by reference, and

d.	the provisions of the State of Mississippi Permit Regulations for the Construction and/or Operation of Air Emissions Equipment (11 Miss. Admin. Code Pt. 2, Ch. 2.), relating to construction permits and synthetic minor operating permits;

2.	any term or condition of any construction permits issued pursuant to Mississippi regulations approved or promulgated through rulemaking under Title I;

3.	any standard or other requirement under Section 111 of the Federal Act, including Section 111(d) which includes Title 40, Part 60 of the Code of Federal Regulations (40 CFR Part 60) and relevant sections of 11 Miss. Admin. Code Pt. 2, Ch. 1.;

4.	any standard or other requirement under Section 112 of the Federal Act, including relevant sections of 11 Miss. Admin. Code Pt. 2, Ch. 1.and 40 CFR Parts 61, 63, and 68;

5.	any standard or other requirement of the acid rain program under Title IV of the Federal Act or the regulations promulgated thereunder, including the State of Mississippi Acid Rain Program Permit Regulations for Purposes of Title IV of the Federal Clean Air Act (11 Miss. Admin. Code Pt. 2, Ch. 7.)  adopted November 17, 1994, and 40 CFR Parts 72, 73, 75, 77, and 78;

6.	any requirements established pursuant to Section 504(b) or Section 114(a)(3) of the Federal Act;

7.	any standard or other requirement governing solid waste incineration under Section 129 of the Federal Act;

8.	any standard or other requirement for consumer and commercial products under Section 183(e) of the Federal Act;

9.	any standard or other requirement for tank vessels under Section 183(f) of the Federal Act;

10.	any standard or other requirement of the program to control air pollution from outer continental shelf sources under Section 328 of the Federal Act;

11.	any standard or other requirement of the regulations promulgated to protect stratospheric ozone under Title VI of the Federal Act;

12.	any national ambient air quality standard or increment or visibility requirement under part C of Title I of the Federal Act.

Each State and Federally-enforceable condition of the draft Title V Operating Permit references the specific relevant requirements of 11 Miss. Admin. Code Pt. 2, Ch. 6. or the applicable requirement upon which it is based. Any condition of the draft Title V permit that is enforceable by the State but is not Federally-enforceable is identified in the draft Title V permit as such.

GREENHOUSE GAS (GHG) APPLICABILITY

In light of the U.S. Supreme Court decision (i.e., Utility Air Regulatory Group v. Environmental Protection Agency, June 23, 2014), MDEQ is following EPA’s guidance memo entitled “Next Steps and Preliminary Views on the Application of Clean Air Act Permitting Programs to Greenhouse Gases…”, dated July 24, 2014.  Therefore GHGs will only be regulated as a part of the NSR/PSD process for new or modified sources that will be major or significant for an NSR regulated pollutant, in addition to GHGs. There are no GHG requirements in the Title V draft permit for this facility.  The facility’s potential-to-emit for CO2e is 1,449,785 TPY.

ACID RAIN PROGRAM APPLICABILITY

Title IV of the Clean Air Act, the Acid Rain Program (40 CFR Parts 72-75), applies to fossil fuel-fired combustors that drive generators for the purpose of generating electricity for sale. Emission Point AA-005 is subject to the Acid Rain Program.  Title IV Acid Rain requirements are addressed in Section 8 of the Title V Operating Permit. In addition, the Acid Rain Permit is attached in the Appendices to the Title V Operating Permit, and the proposed permit includes Acid Rain Program monitoring requirements.

CROSS STATE AIR POLLUTION RULE (CSAPR)

For Emission Points AA-001 through AA-005, the permittee will be required to comply with the provisions of the Cross State Air Pollution Rule (CSAPR) as set forth 40 CFR 97 Subpart BBBBB - TR NOx Ozone Season Trading Program.  The rule establishes an allocation and trading program for ozone season (May 1 – September 30) nitrogen oxides (NOx) emissions that is managed by EPAs Clean Air Markets Division (CAMD). Phase 1 begins for ozone-season NOx trading program on May 1, 2015. The Permittee must ensure that the subject units have allocations equal to or greater than the emissions during the ozone season period.

CAM APPLICABILITY

40 CFR 64 specifies the requirements for Compliance Assurance Monitoring (CAM).  The general applicability is in 40 CFR 64.2 and requires any Part 70 or Part 71 source to comply with the CAM requirements if the following criteria are met:

- The unit is subject to an emission limitation or standard for a regulated air pollutant other than exemptions under 40 CFR 64.2(b)(1), and

- The unit uses a control device to meet the standard, and

- The unit has pre-control emissions exceeding major source thresholds.

Although the facility has equipment that is subject to emissions limits or emission standards and has pre-control emissions exceeding the major source thresholds, no unit uses a control device to comply with an emission limit or standard.  Therefore, CAM does not apply to any unit at this facility.

NSPS APPLICABILITY

Emission Point AA-005, a 1084.6 MMBTU/hr gas-fired Combustion Turbine Generators (CTG), is subject to 40 CFR 60, Subpart GG - Standards of Performance for Stationary Gas Turbines (§60.330-335) since constructed after October 3, 1977.

Emission Point AA-006, a 221.3 MMBTU/hr natural gas-fired boiler, is subject to 40 CFR 60, Subpart Db – Standards of Performance for Industrial-Commercial-Institutional Steam Generating Units since constructed after June 19, 1984.

Emission Point AA-014, a 20 HP propane-fired back-up generator, is subject to 40 CFR 60, Subpart JJJJ – Standards for Stationary Spark Ignition Internal Combustion Engines.

Sources at the facility are not subject to the following NSPS regulations:

- Emission Points AA-001 through AA-004, the gas-fired combustion turbine generators, are not subject to 40 CFR 60, Subpart GG since constructed before October 3, 1977.

- Emission Points AA-001 through AA-005, gas-fired combustion turbines, are not subject to Subpart KKKK since constructed prior to February 18, 2005.

- Emission Points AA-012 and AA-013, 300 HP diesel-fired black start engines, are not subject to Subpart IIII since constructed prior to July 11, 2005.

- Emission Points AA-007 through AA-011, storage tanks, are not subject to Subpart K/Ka/Kb based on size, vapor pressure, and being constructed prior to the applicable compliance dates (June 11, 1973 for K/Ka and July 23, 1984 for Kb).

NESHAP APPLICABILITY

This facility is an area source for HAP emissions (Total HAPs < 25 TPY, Ind. HAPs < 10 TPY).

Emission Points AA-0012 and AA-013, 300 HP black start diesel engines, are subject to 40 CFR 63, Subpart ZZZZ - NESHAP for Stationary Reciprocating Internal Combustion Engines (RICE).  These are considered existing compression ignition (CI) emergency stationary RICE located at an area source and should be in compliance with the applicable requirements of Subpart ZZZZ.

Emission Point AA-014, 20 HP backup propane fired engine, is subject to 40 CFR 63, Subpart ZZZZ, but meets the requirements of this subpart by complying with 40 CFR 60, Subpart JJJJ.

Sources at the facility are not subject to the following NESHAP regulations:

- Emission Point AA-006 combusts only natural gas and is therefore not subject to 40 CFR Part 63, Subpart JJJJJJ - National Emission Standards for Hazardous Air Pollutants (NESHAPS) for Industrial, Commercial, and Institutional Boilers Area Sources.

- Emission Points AA-006 is not subject to Subpart DDDDD – NESHAP for Industrial, Commercial, and Institutional Boilers and Process Heaters since this is not a major source of HAP emissions.

- Emission Points AA-001 through AA-005 are not subject to Subpart YYYY – NESHAP for Stationary Combustion Turbines since this is not a major source of HAP emissions.

- This utility is not subject to Subpart UUUUU.  Combustion turbines are not subject to the standard (63.9983(a)), and the boiler is not subject since it is not considered a coal or oil-fired unit (63.9983(b)).

SPECIFIC APPLICABLE REQUIREMENTS

| EMISSION LIMITS |  |  |  |
| --- | --- | --- | --- |
| Emission Point No. | Pollutant/ Parameter | Draft Permit Emission Limits | Monitoring Requirements |
| AA-001 through AA-006 and AA-012 through AA-014 | SO2 | 4.8 lb/MMBTU | #### Monitor and record fuel type, quantity, and quality monthly. #### Monitor natural gas in accordance with the custom fuel monitoring plan, and RFG (<160 ppmv H2S or 0.0265 lb/MMBTU) will be based on monitoring data collected from Chevron Refinery. |
| AA-001 through AA-004 and AA-006 | PM/PM10 | E=0.8808*I-0.1667 | #### Monitor and record fuel type, quantity, and quality monthly. |
| AA-001 through AA-004 | Fuel Restriction | Natural Gas or Refinery Fuel Gas only | #### Monitor and record fuel type, quantity, quality (sulfur content), and heating value (Btu/ft3) of fuel(s) burned monthly. |
| AA-005 | PM/PM10 | 13.0 lb/hr and 56.9 TPY | #### Perform biennial stack testing to demonstrate compliance. |
| AA-005 | NOX | 60.0 lb/hr and 262.8 TPY, not to exceed 15 ppmvd @ 15% O2 during relative full load operation | #### Monitor and record emissions and parameters (e.g., CEMS) in accordance with 40 CFR Part 75 (e.g., §75.10-18, 20-57, etc.). Install, calibrate, maintain, and operate a continuous monitor (CEMS) to monitor NOX and CO2 emissions (40 CFR Part 75). #### Compliance with the conditions of 40 CFR 75 is considered compliance with NOX monitoring conditions of 40 CFR 60 Subpart GG. The Custom Fuel Monitoring Plan further details this requirement. The CEMS shall be used to meet these requirements of Subpart GG, except that the missing data substitution methodology provided for in 40 CFR Part 75, Subpart D, is not required for purposes of identifying excess emissions. Instead, periods of missing CEMS data shall be reported as monitor downtime in the excess emissions and monitoring performance report required by §60.7(c). Perform biennial stack testing to demonstrate compliance. |
| AA-005 | CO | 19.0 lb/hr and 83.2 TPY | #### Perform biennial stack testing to demonstrate compliance. |
| AA-005 | VOC | 3.0 lb/hr and 13.1 TPY | #### Perform biennial stack testing to demonstrate compliance. |
| AA-005 | Opacity | ≤ 20% | #### Monitoring is not proposed, since only gas is combusted, and the margin of compliance is expected to be high. |
| AA-005 | Fuel Restriction | Natural gas only with sulfur content ≤ 0.8% by weight (8,000 ppmw) | #### Monitor the sulfur content of the fuel used in accordance with the EPA approved Custom Fuel Monitoring Plan. Regardless of this plan, the permittee can maintain records from the supplier that the natural gas meets the definition of natural gas (e.g., ≤ 20.0 grains of total sulfur per 100 standard cubic feet). |
| AA-005 | Startup/ Shutdown | Short-term and long-term emission limits | #### Compliance with short-term emission limits is required, except during periods of startup and shutdown. Compliance with long-term emission limits is required even during periods of startup and shutdown. #### Maintain records of the occurrence and duration of any startup or shutdown, or any periods during which a continuous monitoring system or monitoring device is inoperative. Such records shall include the time and date of such startups and shutdowns. |
| AA-001 through AA-005 | NOX | CSAPR | #### Ensure that the units have allocations for CSAPR |
| AA-006 | NOX | 0.20 lb/MMBTU, not to exceed 42.05 lb/hr and 39.9 TPY | #### Perform biennial stack testing to demonstrate compliance. #### Maintain Emission Point AA-006 fuel usage (in million cubic feet) and annual NOX emissions (in tons per year) during simultaneous operation with Emission Points AA-001 through AA-005. These records shall be recorded for any consecutive 365-day period and reported each calendar quarter. The permittee is subject to the NOX standard under §60.44b, which requires the permittee to install, calibrate, maintain, and operate a CEMS and record the output of the system for measuring NOX and O2 (or CO2) emissions discharged to the atmosphere. |
| AA-006 | Fuel Restriction | Natural gas only (≤ 420 million cf of gas burned per year) | #### In accordance with 40 CFR 60, Subpart Db (60.49b(d)), the permittee shall maintain records of the amount of fuel combusted each day and calculate the annual capacity factor for the reporting period. |
| AA-012 and AA-013 | O&M Practices | O&M Practices | #### Operate and maintain RICE in accordance with manufacturer’s O&M procedures or other approved plan. |

OTHER

N/A