# MISSISSIPPI DEPARTMENT OF ENVIRONMENTAL QUALITY

# Rationale for National Pollutant Discharge Elimination System (NPDES) Permit Reissuance

Kinder Morgan Southeast Terminals LLC, Collins Terminal

Covington County, Mississippi

April 22, 2026

- FACILITY INFORMATION

Facility Name:  Kinder Morgan Southeast Terminals LLC, Collins Terminal

Facility Address:  31 Kola Road, Collins, MS  39428

Water NPDES Water Permit No.: MS0044628

Standard Industrial Classification (SIC):  4226

Permit Writer:  Deanna Rush

EPD Branch:  Water I

- NATURE OF BUSINESS

This facility is a bulk petroleum storage and transfer operation that receives, stores, and distributes refined fuels (gasoline and diesel).  They inject ethanol and butane (depending upon required Reid Vapor Pressure (RVP) but primarily in winter months) into gasoline at the truck loading rack. The   facility’s Standard Industrial Classification (SIC) Code is 4226 (Special Warehousing and Storage, not elsewhere classified). They are a for-hire facility that stores, blends and loads for distribution refined fuels; however, they do not own the fuel. Operations include receipt of refined fuels from pipelines, receipt of additives, ethanol and butane from trucks, transfer of fuels into storage tanks, blending ethanol and butane into gasoline, and loading product into tanker trucks at a truck loading rack. This facility is classified as an NPDES minor source.

- EFFLUENT AND RECEIVING STREAM FLOW DATA

Effluent from the facility’s two outfalls (Outfall 002 and 004) discharge into an unnamed tributary of Okatoma Creek - a tributary of Leaf River in Pascagoula River Basin. The unnamed tributary of Okatoma Creek that receives effluent from the facility has a 7Q10 flow of zero. This is the  lowest stream flow that occurs for seven consecutive days with a statistical probability of happening once every ten years.

Outfall 002: Stormwater runoff from a secondary containment structure (Containment Area 1) and stormwater that could contact product (gasoline, diesel, ethanol) at the truck loading rack.  Truck loading rack contact stormwater goes through an oil water separator and an activated carbon treatment unit before discharging to Containment Area 1 where it mixes with stormwater collected in the bermed containment area. Outfall 002 discharges at a six-month maximum flowrate of 2.3 MGD and a six-month average of 1.47 MGD. Flowrate values are from  June 2025 (EPA ECHO). Containment Area 1 has a surface area of 61,000 Square feet.

Outfall 004: Stormwater from Containment Area 3 and Containment Area 2. Containment Area 3 does not have enough emergency spill capacity to hold a spill of the largest tank in the storage area. Containment Area 2 functions as additional emergency spill capacity in the event of a tank failure. Containment Area 2 drains into Containment Area 3.  Outfall 004 discharges from Containment Area 3 at a six-month maximum flowrate of 3.46 MGD and a six-month average flowrate of 1.47 MGD. Flowrate values are from June 2025 (EPA ECHO). Containment Area 2 and 3 have a combined surface area of 118,000 square feet.

MODIFICATION TO THE PERMIT

The permittee eliminated process wastewater including laboratory sink discharge, monitoring well test water, washdown water, and aquifer characteristics testing water from Outfall 002.  They also eliminated monitor well development water from Outfall 004.

- LIST OF IMPAIRED WATER BODIES (303(d) LIST) and TOTAL MAXIMUM DAILY LOAD (TMDL) REPORTS.

Okatoma Creek is not listed on the 2024 (adopted) nor on the 2026 (Draft) Mississippi List of Impaired Water Bodies (303 (d) List).

TMDL for pH Okatoma creek, Water Body Number MS0410511, TMDL No. 54320 September 26, 2013. The permit contains pH limitations.

Fecal Coliform TMDL for Okatoma Creek Pascagoula River Basin Mississippi (ID 499121506) does not apply because effluent from this facility contains no sanitary wastewater.

- TYPE OF WASTEWATER TREATMENT:

Outfall 002 - Truck rack contact stormwater flows through an oil/water separator and then through an activated carbon unit before discharging into Tank Farm Containment Area 1 where it mixes with stormwater in the basin before discharging through Outfall 002.

Outfall 004 - Stormwater in Containment Area 3 (includes stormwater from Containment Area 2) has no wastewater treatment.

- EPA APPLICABLE CATEGORICAL GUIDELINES

None

DATA FROM APPLICATION FORM (2F) - Outfall 002 and 004

| Pollutant | Outfall 002 | Outfall 004 |
| --- | --- | --- |
|  | Maximum Daily Discharge Concentration | Maximum Daily Discharge Concentration |
| Oil and grease | 4.8 mg/L | 1.5 mg/L |
| Biochemical Oxygen Demand (BOD5) | 15 mg/L | <2 mg/L |
| Chemical Oxygen Demand (COD) | 19.9 mg/L | <4.9 mg/L |
| Total Suspended Solids (TSS) | 11 mg/L | 26 mg/L |
| Total Phosphorus | 0.028 mg/L | 0.035 mg/L |
| Total Kjeldahl Nitrogen (TKN) | <1.89 mg/L | 2.5 mg/L |
| Total Nitrogen (as N) | <2.01 mg/L | <3 mg/L |
| pH (minimum) | 6.5 | 6.3 |
| pH (maximum) | 8.6 | 8.5 |
| Benzene | 0.82 µg/L | <0.82 µg/L |
| BTEX | 0.6630 µg/L | <0.63 µg/L |
| Lead | 2.60 µg/L | N.A. |
| Toluene | 0.87 µg/L | <0.67 µg/L |
| Ethylbenzene | 0.87 µg/L | <0.79 µg/L |

WATER QUALITY LIMITATIONS BASED ON WASTELOAD ALLOCATION

Not Applicable

CATEGORICAL GUIDELINE LIMITATIONS CALCULATIONS

Not Applicable

TOXICITY SCREENING

Not Applicable

ANTIDEGRADATION

The draft permit includes an increase in lead limitations for Outfall 002. Antidegradation does not apply in this case because there was a substantial alteration in effluent, namely the facility no longer discharges process wastewater. The new lead limit was based on acute water quality criteria which is appropriate for stormwater effluent discharging for short durations after rain events.

DRAFT PERMIT CHANGES

- Outfall 002 and Outfall 004 - removed process water streams from outfall descriptions.

- Outfall 002 - increased lead permit limit from 0.00188 mg/L to 0.03 mg/L

PROPOSED FINAL LIMITATIONS

- Average Permit Limitations

| Outfall | Parameter | Categorical Limitation | Water Quality Limitation | Previous Permit Limitation | Proposed Permit Limitation | Monitoring Frequency | Sample Type | DMR Reporting Frequency | 1Basis |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 002 | Flow (MGD) | -- | -- | Report | Report | Quarterly | Estimate | Semi-Annually | PPL |
| 002 | Benzene | -- | -- | 0.05 mg/L | 0.05 mg/L | Quarterly | Grab Sampling | Semi-Annually | PPL |
| 002 | BTEX | -- | -- | 0.75 mg/L | 0.75 mg/L | Quarterly | Grab Sampling | Semi-Annually | PPL |
| 002 | Oil and grease | -- | -- | 10 mg/L | 10 mg/L | Quarterly | Grab Sampling | Semi-Annually | PPL |
| 002 | pH | -- | 6.0 SU | 6.0 SU | 6.0 SU | Quarterly | Grab Sampling | Semi-Annually | MSWQS |
| 002 | Lead, TR | -- | -- | 0.00118 mg/L | Report | Quarterly | Grab Sampling | Semi-Annually | MSWQS |
| 004 | Flow (MGD) | -- | -- | Report | Report | Quarterly | Estimate | Semi-Annually | PPL |
| 004 | Benzene |  |  | 0.05 mg/L | 0.05 mg/L | Quarterly | Grab Sampling | Semi-Annually | PPL |
| 004 | BTEX |  |  | 0.75 mg/L | 0.75 mg/L | Quarterly | Grab Sampling | Semi-Annually | PPL |
| 004 | Oil and grease | -- | -- | 10 mg/L | 10 mg/L | Quarterly | Grab Sampling | Semi-Annually | PPL |
| 004 | pH | -- | 6.0 SU | 6.0 SU | 6.0 SU | Quarterly | Grab Sampling | Semi-Annually | MSWQS |

- Maximum Permit Limitations

| Outfall | Parameter | Categorical Limitation | Water Quality Limitation | Previous Permit Limitation | Proposed Permit Limitation | Monitoring Frequency | Sample Type | DMR Reporting Frequency | 1Basis |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 002 | Flow (MGD) | -- | -- | Report | Report | Quarterly | Estimate | Semi-Annually | PPL |
| 002 | Benzene | -- | -- | 0.075 mg/L | 0.075 mg/L | Quarterly | Grab Sampling | Semi-Annually | PPL |
| 002 | BTEX | -- | -- | 1.12 mg/L | 1.12 mg/L | Quarterly | Grab Sampling | Semi-Annually | PPL |
| 002 | Oil and grease | -- | -- | 15 mg/L | 15 mg/L | Quarterly | Grab Sampling | Semi-Annually | PPL |
| 002 | pH | -- | 9.0 SU | 9.0 SU | 6.0 SU | Quarterly | Grab Sampling | Semi-Annually | MSWQS |
| 002 | Lead, TR |  | 0.03 mg/L | Report | 0.03 mg/L | Quarterly | Grab Sampling | Semi-Annually | MSWQS |
| 004 | Flow (MGD) | -- | -- | Report | Report | Quarterly | Estimate | Semi-Annually | PPL |
| 004 | Benzene |  |  | 0.075 mg/L | 0.075 mg/L | Quarterly | Grab Sampling | Semi-Annually | PPL |
| 004 | BTEX |  |  | 1.12 mg/L | 1.12 mg/L | Quarterly | Grab Sampling | Semi-Annually | PPL |
| 004 | Oil and grease | -- | -- | 15 mg/L | 15 mg/L | Quarterly | Grab Sampling | Semi-Annually | PPL |
| 004 | pH | -- | 9.0 SU | 9.0 SU | 9.0 SU | Quarterly | Grab Sampling | Semi-Annually | MSWQS |

1Basis: MSWQS = Mississippi Water Quality Standards, PPL= Previous Permit Limits. TR = Total Recoverable.  Lead permit limitation changed since effluent is stormwater only and EPD applied acute water quality criteria.