# PERMIT RATIONALE FOR REISSUANCE

Clarksdale Public Utilities, Lewis L Wilkins Generating Station

Coahoma County

Clarksdale, Mississippi

Water NPDES No. MS0001139

August 11, 2026

- FACILITY INFORMATION

Facility Name: 	Clarksdale Public Utilities, Lewis L Wilkins Generating Station

Facility Address: 	240 Hicks Street

Clarksdale, MS  38614

Clarksdale,

Permit No.: 		MS0001139

SIC: 			4911

Permit Writer:  	Tye Gardner

EPD Branch: 		Water I Branch

- NATURE OF BUSINESS

This facility’s Standard Industrial Classification (SIC) codes is 4911 – steam electric generation. The facility is a combined cycle power generation facility which produces 52 MW of electrical power. This facility is classified as an NPDES Minor Source.

- EFFLUENT AND RECEIVING STREAM FLOW DATA

Outfall 001 (External): Effluent consisting of once through cooling water from Unit No. 6, Unit No. 7, Unit No. 9, low volume wastes, and effluent from internal Outfall(s) 101, 201, and 102. These waste streams discharge into the Unit No. 6 discharge pit, Unit No. 7 discharge pit, and Unit No. 9 discharge pit and then to Outfall 001. The outfall has an average flow of 13.75 MGD.

Outfall 002 (External): Effluent consisting of once through cooling water from Unit No. 9, low volume wastes, and effluent from internal Outfall 102. These waste streams discharge into the Unit No. 9 discharge pit and then to Outfall 002. The outfall has an average flow of 5.76 MGD.

Outfall 102 (Internal): From the January 1, 2026 application, Outfall 102 consists of Outfall 102a and Outfall 102b. Effluent consisting of low volume wastes. The low volume wastes from Outfall 102b include No. 9 HRSG blowdown, noncontact cooling water from the air compressor, and waste water from floor drains. The low volume waste from Outfall 102a include demineralizer waste water. These waste streams discharge into the Unit No. 9 discharge pit and then to Outfall(s) 002 and 001. This outfall has an average flow of 0.02242 MGD.

Outfall 101 (Internal):	Effluent from this outfall consists of low volume wastes. The low volume wastes include Unit No. 7 boiler blowdown, noncontact cooling water from the Unit No. 7 condenser. These waste streams discharge into the Unit No. 6 and Unit No. 7 discharge pits and then to Outfall 001. This outfall has an average flow of 5.535 MGD.

Outfall 201 (Internal):	Effluent from this outfall consists of low volume wastes. The low volume wastes include No. 6 HRSG boiler blowdown. This waste stream discharges into the Unit No. 6 and Unit No. 7 discharge pits and then to Outfall 001. This outfall has an average flow of 0.005 MGD.

Wastewater from these outfalls discharge to an unnamed ditch thence into Big Sunflower River. The Big Sunflower River is located in the Yazoo River Basin. This stream is classified as “fish and Wildlife”.

It should be noted that for Unit No. 9 Outfall(s) 002 and 001 outlet pipes from the sump are at the same level. Any flow from Unit No. 9 would discharge from Outfall(s) 002 and 001 equally.

It should be noted that the effluent flow from external outfall(s) 001 and 002 are composed primarily (combined total of approximately 99.8%) of once through cooling water. Because of this, Categorical limitations for once through cooling water were applied to those outfalls.

- 303(d) and TOTAL MAXIMUM DAILY LOAD (TMDL) ISSUES

Big Sunflower River does not appear on the 2026 303(d) List of Impaired Water Bodies.

The facility complies with the following applicable TMDLs:

- Fecal Coliform – Big Sunflower River – Sunflower, Coahoma, Washington, and Humphreys Counties – October 2002 – ID: 902101501

- Fecal Coliform – Big Sunflower River and Little Sunflower River – Coahoma and Sunflower Counties – December 2010

- Legacy Pesticides, DDT, and Toxaphene – Yazoo River Basin – May 2003 – ID: 903051601

- Legacy Pesticides, DDT, and Toxaphene – Yazoo River Basin – November 2005 – ID: 905110401

- Organic Enrichment, Nutrients, and Sediment – Big Sunflower River – Sunflower, Coahoma, Washington, Humphreys, and Sharkey Counties – June 2003 – ID: 903063003

- Sediment – Delta Region – Yazoo River Basin – April 2008 – ID: 908041702

- Total Nitrogen and Total Phosphorus – Selected Large Rivers in the Delta – Yazoo River Basin – June 2008 – ID: 908063054

- TYPE OF WASTEWATER TREATMENT

None

- EPA APPLICABLE CATEGORICAL GUIDELINES

40 CFR 423 – Steam Electric Power Generation Point Source Category; Section 423.12 (BPT) and 423.13 (BAT).

VII.	DATA FROM APPLICATION FORM (2C)

Outfall 001 	Outfall 002

| Parameter | 1Max. | 2LTA | 3# |  | Parameter | 1Max. | 2LTA | 3# |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| BOD5, mg/L | < 4 | -- | 1 |  | BOD5, mg/L | < 5 | -- | 1 |
| COD, mg/L | < 10 | -- | 1 |  | COD, mg/L | < 15 | -- | 1 |
| TOC, mg/L | < 5 | -- | 1 |  | TOC, mg/L | < 5 | -- | 1 |
| TSS, mg/L | 19 | -- | 1 |  | TSS, mg/L | 26 | -- | 1 |
| Ammonia, mg/L | 0.33 | -- | 1 |  | Ammonia, mg/L | 0.299 | -- | 1 |
| Flow, MGD | 11.5 | 4.55 | 19 |  | Flow, MGD | 7.99 | -- | 18 |
| Temperature (w), ºC | 18 | -- | 21 |  | Temperature (w), ºC | 21 | -- | 1 |
| Temperature (s), ºC | 33 | -- | 21 |  | Temperature (s), ºC | 21 | -- | 1 |
| pH, SU (max) | 8.9 | -- | 21 |  | pH, SU (max) | 9.0 | -- | 1 |
| Nitrate-Nitrite, mg/L | 0.6 | -- | 1 |  | Nitrate-Nitrite, mg/L | <0.1 | -- | 1 |
| Oil and Grease, mg/L | ND | -- | 1 |  | Oil and Grease, mg/L | ND | -- | 1 |
| Nitrogen (as N), mg/L | 0.73 | -- | 1 |  | Nitrogen (as N), mg/L | <0.5 | -- | 1 |
| Phosphorus (as P), mg/L | 0.27 | -- | 1 |  | Phosphorus (as P), mg/L | 0.604 | -- | 1 |
| Sulfate, mg/L | 17 | -- | 1 |  | Sulfate, mg/L | 12.8 | -- | 1 |
| Iron, mg/L | 17.04 | 3.86 | 19 |  | Iron, mg/L | 6.99 | 4.39 | 16 |
| Manganese, mg/L | 0.42 | -- | 1 |  | Manganese, mg/L | 0.534 | -- | 1 |
| Mercury, mg/L | 2.2e-4 | -- | 1 |  | Mercury, mg/L | 2.0e-4 | -- | 1 |
| Selenium, mg/L | <0.05 | -- | 1 |  | Selenium, mg/L | <0.05 | -- | 1 |
| Cyanide, mg/L | <0.05 | -- | 1 |  | Cyanide, mg/L | <0.05 | -- | 1 |
|  |  |  |  |  | Zinc, mg/L | <0.02 | <0.02 | 12 |

Outfall 101 		Outfall 201

| Parameter | 1Max. | 2LTA | 3# |  | Parameter | 1Max. | 2LTA | 3# |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| BOD5, mg/L | < 4 | -- | 1 |  | BOD5, mg/L | < 4 | -- | 1 |
| COD, mg/L | < 10 | -- | 1 |  | COD, mg/L | < 10 | -- | 1 |
| TOC, mg/L | < 5 | -- | 1 |  | TOC, mg/L | < 5 | -- | 1 |
| TSS, mg/L | 25 | -- | 1 |  | TSS, mg/L | 210 | -- | 1 |
| Ammonia, mg/L | 0.43 | -- | 1 |  | Ammonia, mg/L | 0.43 | -- | 1 |
| Flow, MGD | 0.005 | -- | 1 |  | Flow, MGD | 0.005 | -- | 1 |
| Temperature (w), ºC | 21 | -- | 1 |  | Temperature (w), ºC | 21 | -- | 1 |
| Temperature (s), ºC | 21 | -- | 1 |  | Temperature (s), ºC | 21 | -- | 1 |
| pH, SU (max) | 9.0 | -- | 18 |  | pH, SU (max) | 11.35 | -- | 1 |
| Nitrate-Nitrite, mg/L | 0.8 | -- | 1 |  | Nitrate-Nitrite, mg/L | 0.8 | -- | 1 |
| Oil and Grease, mg/L | ND | -- | 1 |  | Oil and Grease, mg/L | 3.43 | -- | 1 |
| Nitrogen (as N), mg/L | 2.42 | -- | 1 |  | Nitrogen (as N), mg/L | 2.42 | -- | 1 |
| Phosphorus (as P), mg/L | 0.14 | -- | 1 |  | Phosphorus (as P) mg/L | 0.14 | -- | 1 |
| Sulfate, mg/L | 5.0 | -- | 1 |  | Sulfate, mg/L | 5 | -- | 1 |
| Iron, mg/L | 8.015 | 4.39 | 16 |  | Iron, mg/L | 8.015 | 4.39 | 16 |
| Manganese, mg/L | 0.52 | -- | 1 |  | Manganese, mg/L | 0.52 | -- | 1 |
| Mercury, mg/L | 2.8e-4 | -- | 1 |  | Mercury, mg/L | 2.8e-4 | -- | 1 |
| Selenium, mg/L | ND | -- | 1 |  | Selenium, mg/L | ND | -- | 1 |
| Cyanide, mg/L | ND | -- | 1 |  | Cyanide, mg/L | ND | -- | 1 |

Outfall 102

| Parameter | 1Max. | 2LTA | 3# |  |
| --- | --- | --- | --- | --- |
| BOD5, mg/L | < 4 | -- | 1 |  |
| COD, mg/L | < 10 | -- | 1 |  |
| TOC, mg/L | < 5 | -- | 1 |  |
| TSS, mg/L | 25 | -- | 1 |  |
| Ammonia, mg/L | 0.43 | -- | 1 |  |
| Flow, MGD | 0.017 | -- | 1 |  |
| Temperature (w), ºC | 18 | -- | 1 |  |
| Temperature (s), ºC | 33 | -- | 1 |  |
| pH, SU (max) | 8.9 | -- | 18 |  |
| Nitrate-Nitrite, mg/L | 0.60 | -- | 1 |  |
| Oil and Grease, mg/L | 1.14 | -- | 1 |  |
| Nitrogen (as N), mg/L | 0.73 | -- | 1 |  |
| Phosphorus (as P), mg/L | 0.27 | -- | 1 |  |
| Sulfate, mg/L | 5.0 | -- | 1 |  |
| Iron, mg/L | 8.015 | 4.39 | 16 |  |
| Manganese, mg/L | 0.52 | -- | 1 |  |
| Mercury, mg/L | 2.2e-4 | -- | 1 |  |
| Selenium, mg/L | ND | -- | 1 |  |
| Cyanide, mg/L | ND | -- | 1 |  |

#### VIII. 	WATER QUALITY LIMITATIONS BASED ON WASTELOAD ALLOCATION

Not Applicable

- CATEGORICAL GUIDELINE LIMITATIONS CALCULATIONS

Not Applicable

TOXICITY SCREENING

See Attachment B

- XI.	PROPOSED FINAL LIMITATIONS

- Average Permit Limitations

| Outfall | Parameter | Categorical Limitation | Water Quality Limitation | Present Permit Limitation | Proposed Permit Limitation | Monitoring Frequency | Sample Type | DMR Reporting Frequency | 1Basis |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 001 | Flow (MGD) | -- | -- | Report | Report | Continuously | Continuous Recorder | Monthly | TJ |
| 001 | Chlorine, TR2 | -- | 0.011 mg/L | 0.011 mg/L | 0.011 mg/L | Twice per month | Multiple Grab5 | Monthly | MSWQS |
| 001 | Iron, TR2 | -- | -- | Report | Report | Twice per month | 8-hr Composite | Monthly | TJ |
| 001 | Temperature (°F) | -- | -- | Report | Report | Twice per month | Grab Sampling | Monthly | TJ |
| 001 | pH | -- | 6.0 SU | 6.5 SU | 6.0 SU | Twice per month | Grab Sampling | Monthly | MSWQS |
| 002 | Flow (MGD) | -- | -- | Report | Report | Continuously | Continuous Recorder | Monthly | TJ |
| 002 | Chlorine, TR2 | -- | 0.011 mg/L | 0.011 mg/L | 0.011 mg/L | Twice per month | Multiple Grab5 | Monthly | MSWQS |
| 002 | Iron, TR | -- | -- | Report | Report | Twice per month | 8-hr Composite | Monthly | TJ |
| 002 | Temperature (°F) | -- | -- | Report | Report | Twice per month | Grab Sampling | Monthly | TJ |
| 002 | pH | -- | 6.0 SU | 6.5 SU | 6.0 SU | Twice per month | Grab Sampling | Monthly | MSWQS |
| 102 | Flow (MGD) | -- | -- | Report | Report | Monthly | Instantaneous | Monthly | TJ |
| 102 | Oil and Grease | 15 mg/L | -- | 15 mg/L | 15 mg/L | Monthly | Grab Sampling | Monthly | Categorical |
| 102 | TSS | 30 mg/L | -- | 30 mg/L (18 lb/day) | 30 mg/L (18 lb/day) | Monthly | Grab Sampling | Monthly | Categorical |
| 102 | pH | -- | 6.0 SU | 6.0 SU | 6.0 SU | Monthly | Grab Sampling | Monthly | MSWQS |
| 101 | Flow (MGD) | -- | -- | Report | Report | Monthly | Instantaneous | Quarterly | TJ |
| 101 | Oil and Grease | 15 mg/L | -- | 15 mg/L | 15 mg/L | Monthly | Grab Sampling | Quarterly | Categorical |
| 101 | TSS | 30 mg/L | -- | 30 mg/L (18 lb/day) | 30 mg/L (18 lb/day) | Monthly | Grab Sampling | Quarterly | Categorical |
| 101 | pH | -- | 6.0 SU | 6.0 SU | 6.0 SU | Monthly | Grab Sampling | Quarterly | MSWQS |
| 201 | Flow (MGD) | -- | -- | Report | Report | Monthly | Instantaneous | Quarterly | TJ |
| 201 | Oil and Grease | 15 mg/L | -- | 15 mg/L | 15 mg/L | Monthly | Grab Sampling | Quarterly | Categorical |
| 201 | TSS | 30 mg/L | -- | 30 mg/L (18 lb/day) | 30 mg/L (18 lb/day) | Monthly | Grab Sampling | Quarterly | Categorical |
| 201 | pH | -- | 6.0 SU | 6.0 SU | 6.0 SU | Monthly | Grab Sampling | Quarterly | MSWQS |

- Maximum Permit Limitations

| Outfall | Parameter | Categorical Limitation | Water Quality Limitation | Present Permit Limitation | Proposed Permit Limitation | Monitoring Frequency | Sample Type | DMR Reporting Frequency | 1Basis |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 001 | Flow (MGD) | -- | -- | Report | Report | Continuously | Continuous Recorder | Monthly | TJ |
| 001 | Chlorine, TR2 | -- | 0.019 mg/L | 0.019 mg/L | 0.019 mg/L | Twice per month | Multiple Grab5 | Monthly | MSWQS |
| 001 | Chlorination Duration | 120 min/unit | -- | 120 min/unit | 120 min/unit | Daily | Measurement | Monthly | Categorical |
| 001 | Iron, TR2 | -- | -- | Report | Report | Twice per month | 8r-Composite | Monthly | TJ |
| 001 | Temperature (°F) | -- | 90 | 90 | 90 | Twice per month | Grab Sampling | Monthly | MSWQS |
| 001 | pH | -- | 9.0 SU | 9.0 SU | 9.0 SU | Twice per month | Grab Sampling | Monthly | MSWQS |
| 002 | Flow (MGD) | -- | -- | Report | Report | Continuously | Continuous Recorder | Monthly | TJ |
| 002 | Chlorine, TR2 | -- | 0.019 mg/L | 0.019 mg/L | 0.019 mg/L | Twice per month | Multiple Grab5 | Monthly | MSWQS |
| 002 | Chlorination Duration | 120 min/unit | -- | 120 min/unit | 120 min/unit | Daily | Measurement | Monthly | Categorical |
| 002 | Iron, TR2 | -- | -- | Report | Report | Twice per month | 8r-Composite | Monthly | TJ |
| 002 | Temperature (°F) | -- | 90 | 90 | 90 | Twice per month | Grab Sampling | Monthly | MSWQS |
| 002 | pH | -- | 9.0 SU | 9.0 SU | 9.0 SU | Twice per month | Grab Sampling | Monthly | MSWQS |
| 102 | Flow (MGD) | -- | -- | Report | Report | Monthly | Instantaneous | Monthly | TJ |
| 102 | Oil and Grease | 20 mg/L | -- | 20 mg/L | 20 mg/L | Monthly | Grab Sampling | Monthly | Categorical |
| 102 | TSS | 100 mg/L | -- | 100 mg/L | 100 mg/L | Monthly | Grab Sampling | Monthly | Categorical |
| 102 | pH | -- | 9.0 SU | 9.0 SU | 9.0 SU | Monthly | Grab Sampling | Monthly | MSWQS |
| 101 | Flow (MGD) | -- | -- | Report | Report | Monthly | Instantaneous | Quarterly | TJ |
| 101 | Oil and Grease | 20 mg/L | -- | 20 mg/L | 20 mg/L | Monthly | Grab Sampling | Quarterly | Categorical |
| 101 | TSS | 100 mg/L | -- | 100 mg/L | 100 mg/L | Monthly | Grab Sampling | Quarterly | Categorical |
| 101 | pH | -- | 9.0 SU | 9.0 SU | 9.0 SU | Monthly | Grab Sampling | Quarterly | MSWQS |
| 201 | Flow (MGD) | -- | -- | Report | Report | Monthly | Instantaneous | Quarterly | TJ |
| 201 | Oil and Grease | 20 mg/L | -- | 20 mg/L | 20 mg/L | Monthly | Grab Sampling | Quarterly | Categorical |
| 201 | TSS | 100 mg/L | -- | 100 mg/L | 100 mg/L | Monthly | Grab Sampling | Quarterly | Categorical |
| 201 | pH | -- | 9.0 SU | 9.0 SU | 9.0 SU | Monthly | Grab Sampling | Quarterly | MSWQS |

1Basis: 11 Miss. Pt. 6, Ch.1 = 11 Miss. Admin Code Pt. 6, Ch.1, Categorical = 40 CFR Part 423 Steam Electric Power Generation Point Source Category; Section 423.15 New  Source Performance Standards (NSPS),  MSWQS = Mississippi Water Quality Standards, TJ = Technical Judgement.

2TR =Total Residual		4TR = Total Recoverable

3FA = Free Available	5Multiple Grab

Report Submittal Requirement

Discharges from the following outfalls failed the toxicity screen because of a variability factor, i.e. only one sample was provided on the application. Based on technical judgment, the permittee will be required to monitor each outfall monthly when discharging until 12 effluent samples have been analyzed for each outfall.

- Outfall 001 – total recoverable selenium, total recoverable arsenic

- Outfall 002 – total recoverable selenium, total recoverable arsenic, total recoverable zinc

If this data indicates a violation of water quality standards, the NPDES permit may be reopened and modified. Once all 12 samples have been collected for each pollutant, the permittee shall submit a report summarizing the results.

ATTACHMENT B

TOXICITY SCREENING

This facility discharges into the Big Sunflower River that has a 7Q10 flow of 19.39 MGD (30 cfs) and a Mean Annual stream flow of 81.64 MGD (126.32 cfs).  A toxicity screen is performed on all pollutant data provided in the application that has an applicable state and/or national water quality standard.  A NRWQC of 100 ug/L (0.1 mg/L) is listed for manganese; however, this standard was originally recommended in the Red Book and subsequently published in the Gold Book for marine water in order to protect against a possible human health hazard to humans by manganese accumulation in shellfish. Because the Big Sunflower River is a freshwater stream, this standard is not applicable and a toxicity screen will not be performed on this pollutant.

The effluent flow information used to calculate these limits was taken from the permit renewal application (EPA Form 2C). The receiving stream flow information was provided by our Water Quality Modeling/TMDLBranch.

Stream Flow:

Qr	= 7Q10 of receiving stream (Acute and Chronic Screenings)

=  19.39 MGD

Qr	= Mean Annual Flow (Human Health Screening)

= 81.64 MGD

Effluent Flow:

Qw	= Maximum 30 day flow (Outfall 001)

= 11.5 MGD (Outfall 001- Maximum daily value is used in the screen because the Maximum 30 day flow value is not available).

= 5.545 MGD (Outfall 002 - Taken from the August 2019 DMR)

IWC	(%) = 39.21% (Provided on the Waste Load Allocation)

Xt =  (Qr * Xr) + (Qw * Xw)

(Qr + Qw)

Xr	= Receiving stream concentration.

Xw 	= Historical effluent data from the application.

Xwa	= Permit limits from previous permit or from effluent guidelines.

Xta	= The calculated in-stream concentration based on existing permit limits or the calculated limit based on current effluent guidelines.

Xt	= The calculated in-stream concentration is based on historical effluent data from the application.

Note:       To calculate Xta substitute Xwa for Xw.

Until 12 samples can be analyzed, the effluent is multiplied by 10 as seen in the following equation:

Xt = (Qr * Xr) + (Qw * Xw  * 10)

(Qr + Qw)

To view screening results, see the toxicity screening tables on the following pages.

*Calculations completed in 2020. All 12 samples have not been acquired as of July 20, 2026.